## iocosts
~IN |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
enr_inst_cpcy_p | 100 | MW | installed capacity | bdg_1000_envr_ct | 0 | $ | lands, resettlements, relocations and other socialenvironmental cost
pwh_strc_slex_m3 | 4000 | m³ | common excavation volume of the powerhouse | bdg_1100_pwhc_ct | 5811552 | $ | powerhouse civil and related land development cost
pwh_strc_rkex_m3 | 10000 | m³ | surface rock excavation volume of the powerhouse | bdg_1200_dmhs_ct | 19331058.816 | $ | dams and hydraulic system cost
pwh_strc_ugex_m3 | 0 | m³ | underground rock excavation volume of the powerhouse | bdg_1210_div0_ct | 1293318.38 | $ | diversion cost
pwh_strc_trtm_m2 | 500 | m² | foundation cleaning and treatment area of the powerhouse | bdg_1220_dam0_ct | 964114.2 | $ | dams and dikes cost
pwh_strc_conc_m3 | 8000 | m³ | structural concrete volume of the powerhouse | bdg_1230_spw0_ct | 4193529.3 | $ | spillway cost
pwh_misc_ldev_ct | 929000 | $ | land developments cost | bdg_1240_hsy0_ct | 9658253.8 | $ | intakes and adduction cost
pwh_misc_inst_ct | 1250000 | $ | installations and final works cost | bdg_1250_oth0_ct | 0 | $ | special constructions cost
pwh_turb_totl_n | 2 |  | number of turbines | bdg_1300_eqp0_ct | 48146400 | $ | turbines and generators cost
pwh_turb_0000_ct | 7180000 | $ | turbine cost | bdg_1400_elet_ct | 10399622.4 | $ | auxiliary electrical equipment cost
pwh_genr_totl_n | 2 |  | number of generators | bdg_1500_mech_ct | 6808540.8 | $ | miscellaneous mechanical equipment cost
pwh_genr_0000_ct | 12580000 | $ | generator cost | bdg_1600_road_ct | 3540360 | $ | roads, railroads and bridges cost
pwh_dtub_slog_n | 2 |  | number of stoplogs of the draft tube | bdg_totl_drct_ct | 94037534.016 | $ | direct cost
pwh_dtub_slog_ct | 84000 | $ | stoplogs cost of the draft tube | bdg_1700_indt_ct | 12412954.4901 | $ | indirect cost
pwh_dtub_fwgt_n | 0 |  | number of fixed wheel gates of the draft tube | bdg_totl_0000_ct | 106450488.5061 | $ | total cost without interest during construccion
pwh_dtub_fwgt_ct | 0 | $ | fixed wheel gates cost of the draft tube | bdg_1800_intr_ct | 12774058.6207 | $ | interest during construccion
pwh_strc_brdg_ct | 922000 | $ | bridge crane cost | bdg_totl_intr_ct | 119224547.1268 | $ | total cost with interest during construccion
pwh_dtub_gtry_ct | 1863000 | $ | gantry crane cost | bdg_totl_civl_ct | 17496570.816 | $ | total civil cost
pwh_dtub_embp_ct | 434000 | $ | embedded parts cost of the draft tube equipment | bdg_totl_eqp0_ct | 76540963.2 | $ | equipment cost
div_cfd1_fill_m3 | 0 | m³ | total volume of the first phase cofferdam | bdg_totl_indx_ct | 1192.2455 | $ | index cost
div_cfd2_fill_m3 | 1000 | m³ | total volume of the second phase cofferdam
div_chan_slex_m3 | 1600 | m³ | common excavation volume of the diversion channels
div_chan_rkex_m3 | 400 | m³ | surface rock excavation volume of the diversion channels
div_chan_regc_m3 | 500 | m³ | dental concrete volume for the regularization of the diversion channels
div_tund_ugex_m3 | 3000 | m³ | underground rock excavation volume of the channels of the diversion tunnel
div_tund_trtm_m2 | 100 | m² | foundation cleaning and treatment area of the diversion tunnel
div_tund_conc_m3 | 400 | m³ | structural concrete volume of the diversion tunnels (including intake)
div_tund_shot_m3 | 300 | m³ | shotcrete volume of the diversion tunnels
div_tund_fwgt_n | 1 |  | number of fixed wheel gates of the diversion tunnel
div_tund_fwgt_ct | 358000 | $ | fixed wheel gates cost of the diversion tunnel
div_tund_slog_n | 1 |  | number of stoplogs of the diversion tunnel
div_tund_slog_ct | 258000 | $ | stoplogs cost of the diversion tunnel
div_tund_embp_ct | 152000 | $ | embedded parts cost of the diversion tunnel equipment
div_gall_rkex_m3 | 0 | m³ | surface rock excavation volume of the diversion gallery
div_gall_trtm_m2 | 0 | m² | foundation cleaning and treatment area of the diversion gallery
div_gall_conc_m3 | 0 | m³ | structural concrete volume of the diversion gallery (including intake)
div_slui_rkex_m3 | 0 | m³ | surface rock excavation volume of the sluiceway
div_slui_trtm_m2 | 0 | m² | foundation cleaning and treatment area of the sluiceway
div_slui_conc_m3 | 0 | m³ | structural concrete volume of the sluiceway
div_g0s0_fwgt_n | 0 |  | number of fixed wheel gates of the diversion gallery or sluiceway
div_g0s0_fwgt_ct | 0 | $ | fixed wheel gates cost of the diversion gallery or sluiceway
div_g0s0_slog_n | 0 |  | number of stoplogs of the diversion gallery or sluiceway
div_g0s0_slog_ct | 0 | $ | stoplogs cost of the diversion gallery or sluiceway
div_slui_slog_n | 0 |  | number of downstream stoplogs of the sluiceway
div_slui_slog_ct | 0 | $ | downstream stoplogs cost of the sluiceway
div_g0s0_embp_ct | 0 | $ | embedded parts cost of the diversion gallery or sluiceway equipment
dam_eart_slex_m3 | 0 | m³ | common excavation volume of an earthfill dam
dam_eart_trtm_m2 | 0 | m² | foundation cleaning and treatment area of an earthfill dam
dam_rock_slex_m3 | 0 | m³ | common excavation volume of a rockfill dam
dam_rock_trtm_m2 | 0 | m² | foundation cleaning and treatment area of a rockfill dam
dam_eart_fill_m3 | 0 | m³ | compacted earthfill volume of the earthfill dam
dam_rock_fill_m3 | 16000 | m³ | rockfill volume of the rockfill dam
dam_rock_clay_m3 | 8000 | m³ | clay core volume of the rockfill dam
dam_rock_tran_m3 | 0 | m³ | transitions volumes of a rockfill dam
dam_eart_filt_m3 | 0 | m³ | filters and transitions volumes of an earthfill dam
dam_rock_conc_m3 | 0 | m³ | concrete face volume of the rockfill dam
dam_eart_ripr_m3 | 0 | m³ | rip-rap volume of the earthfill dam
dam_eart_prot_m2 | 0 | m² | dam downstream face protection of the earthfill dam
dam_conc_slex_m3 | 0 | m³ | common excavation volume of the concrete dam
dam_conc_rkex_m3 | 0 | m³ | surface rock excavation volume of the concrete dam
dam_conc_trtm_m2 | 0 | m² | foundation cleaning and treatment area of the concrete dam
dam_conc_conc_m3 | 0 | m³ | structural concrete volume of the concrete dam
dam_conc_hcr0_m3 | 0 | m³ | roller-compacted concrete volume of the concrete dam
dam_trwl_slex_m3 | 1000 | m³ | common excavation volume of the transition walls
dam_trwl_rkex_m3 | 3000 | m³ | surface rock excavation volume of the transition walls
dam_trwl_trtm_m2 | 2000 | m² | foundation cleaning and treatment area of the transition walls
dam_trwl_conc_m3 | 4000 | m³ | structural concrete volume of the transition walls
spw_appr_slex_m3 | 0 | m³ | common excavation volume of the spillway approach channel
spw_appr_rkex_m3 | 0 | m³ | surface rock excavation volume of the spillway approach channel
spw_appr_regc_m3 | 0 | m³ | dental concrete volume for the regularization of the spillway approach channel
spw_rest_slex_m3 | 0 | m³ | common excavation volume of the spillway restitution channel
spw_rest_rkex_m3 | 0 | m³ | surface rock excavation volume of the spillway restitution channel
spw_rest_regc_m3 | 0 | m³ | dental concrete volume for the regularization of the spillway restitution channel
spw_totl_slex_m3 | 1500 | m³ | common excavation volume of the spillway
spw_totl_rkex_m3 | 4500 | m³ | surface rock excavation volume of the spillway
spw_totl_trtm_m2 | 2000 | m² | foundation cleaning and treatment area of the spillway
spw_totl_conc_m3 | 10000 | m³ | structural concrete volume of the spillway
spw_ogee_segm_n | 2 |  | number of segment gates of the spillway
spw_ogee_segm_ct | 429000 | $ | segment gates cost of the spillway
spw_ogee_slog_n | 1 |  | number of stoplogs of the spillway
spw_ogee_slog_ct | 186000 | $ | stoplogs cost of the spillway
spw_ogee_cran_ct | 268000 | $ | crane cost of the spillway
spw_ogee_embp_ct | 188000 | $ | embedded parts cost of the spillway equipment
hsy_inch_slex_m3 | 0 | m³ | common excavation volume of the intake channel
hsy_inch_rkex_m3 | 0 | m³ | surface rock excavation volume of the intake channel
hsy_inch_regc_m3 | 0 | m² | dental concrete volume for the regularization of the intake channel
hsy_infb_fwgt_n | 2 |  | number of fixed wheel gates of the forebay intake
hsy_infb_fwgt_ct | 150000 | $ | fixed wheel gates cost of the forebay intake
hsy_infb_slog_n | 1 |  | number of stoplogs of the forebay intake
hsy_infb_slog_ct | 15000 | $ | stoplogs cost of the forebay intake
hsy_infb_cran_ct | 70000 | $ | crane cost of the forebay intake
hsy_infb_rack_ct | 350000 | $ | trash racks cost of the forebay intake
hsy_infb_embp_ct | 120000 | $ | embedded parts cost of the forebay intake equipment
hsy_intk_slex_m3 | 400 | m³ | common excavation volume of the intake
hsy_intk_rkex_m3 | 700 | m³ | surface rock excavation volume of the intake
hsy_intk_trtm_m2 | 100 | m² | foundation cleaning and treatment area of the intake
hsy_intk_conc_m3 | 1000 | m³ | structural concrete volume of the intake
hsy_intk_fwgt_n | 2 |  | number of fixed wheel gates of the intake
hsy_intk_fwgt_ct | 173000 | $ | fixed wheel gates cost of the intake
hsy_intk_slog_n | 1 |  | number of stoplogs of the intake
hsy_intk_slog_ct | 20000 | $ | stoplogs cost of the intake
hsy_intk_cran_ct | 95000 | $ | crane cost of the intake
hsy_intk_rack_ct | 401000 | $ | trash racks cost of the intake
hsy_intk_embp_ct | 170000 | $ | embedded parts cost of the intake equipment
hsy_chan_slex_m3 | 0 | m³ | common excavation volume of the headrace channel
hsy_fbay_slex_m3 | 0 | m³ | common excavation volume of the forebay
hsy_chan_regc_m3 | 0 | m³ | dental concrete volume for the regularization of headrace channel
hsy_chan_rkex_m3 | 0 | m³ | surface rock excavation volume of the headrace channel
hsy_fbay_rkex_m3 | 0 | m³ | surface rock excavation volume of the forebay
hsy_chan_trtm_m2 | 10000 | m² | foundation cleaning and treatment area of the headrace channel
hsy_fbay_trtm_m2 | 550 | m² | foundation cleaning and treatment area of the forebay
hsy_chan_conc_m3 | 0 | m³ | structural concrete volume of the headrace channel
hsy_fbay_conc_m3 | 0 | m³ | structural concrete volume of the forebay
hsy_chan_shot_m3 | 0 | m³ | shotcrete volume of the headrace channel
hsy_lpps_slex_m3 | 0 | m³ | common excavation volume of the low pressure penstock
hsy_lpps_rkex_m3 | 0 | m³ | surface rock excavation volume of the low pressure penstock
hsy_tunl_ugex_m3 | 4000 | m³ | underground rock excavation volume of the low pressure tunnel
hsy_tunl_trtm_m2 | 1000 | m² | foundation cleaning and treatment area of the low pressure tunnel
hsy_lpps_trtm_m2 | 0 | m² | foundation cleaning and treatment area of the low pressure penstock
hsy_tunl_conc_m3 | 600 | m³ | concrete volume of the low pressure tunnel
hsy_lpps_conc_m3 | 0 | m³ | structural concrete volume of the low pressure penstock
hsy_tunl_shot_m3 | 1600 | m³ | shotcrete volume of the low pressure tunnel
hsy_stnk_slex_m3 | 200 | m³ | common excavation volume of the surge tank
hsy_stnk_rkex_m3 | 400 | m³ | surface rock excavation volume of the surge tank
hsy_stnk_ugex_m3 | 600 | m³ | underground rock excavation volume of the surge tank
hsy_stnk_trtm_m2 | 0 | m² | foundation cleaning and treatment area of the surge tank
hsy_stnk_conc_m3 | 100 | m³ | structural concrete volume of the surge tank
hsy_stnk_stee_t | 0 | t | steel lining of the surge tank
hsy_pstk_slex_m3 | 400 | m³ | common excavation volume of the penstock
hsy_pstk_rkex_m3 | 2000 | m³ | surface rock excavation volume of the penstock
hsy_tunp_ugex_m3 | 3000 | m³ | underground rock excavation volume of the high pressure tunnel
hsy_tunp_trtm_m2 | 1000 | m² | foundation cleaning and treatment area of the high pressure tunnel
hsy_pstk_trtm_m2 | 10000 | m² | foundation cleaning and treatment area of the penstock blocks
hsy_tunp_conc_m3 | 200 | m³ | concrete volume of the high pressure tunnel
hsy_pstk_conc_m3 | 300 | m³ | structural concrete volume of the penstock blocks
hsy_pstk_stee_t | 589 | t | weight of the steel lined penstock
pwh_valv_bfly_n | 2 |  | number of butterfly valves
pwh_valv_bfly_ct | 1700000 | $ | butterfly valve cost
pwh_valv_sphr_n | 0 |  | number of spherical valves
pwh_valv_sphr_ct | 0 | $ | spherical valve cost
hsy_trce_slex_m3 | 200 | m³ | common excavation volume of the tailrace
hsy_trce_rkex_m3 | 400 | m³ | surface rock excavation volume of the tailrace
hsy_trce_ugex_m3 | 0 | m³ | underground rock excavation volume of the tailrace
hsy_trce_trtm_m2 | 100 | m² | foundation cleaning and treatment area of the tailrace
hsy_trce_conc_m3 | 0 | m³ | structural concrete volume of the tailrace
hsy_trce_regc_m3 | 0 | m² | dental concrete volume for the regularization of the tailrace
oth_port_lock_ct | 0 | $ | port or lock system cost
oth_fish_tran_ct | 0 | $ | fish transfer system cost
oth_accs_road_l | 2 | km | length of the access roads
oth_accs_brdg_l | 100 | m | length of the access bridges
hera_env_res0_rurl_a | 0 | ha | rural properties affected by the reservoir
hera_env_res0_urbn_a | 0 | ha | urban properties affected by the reservoir
hera_env_res0_clea_a | 0 | ha | reservoir cleaning area
hera_env_res0_ppa0_a | 0 | ha | permanent preservation areas
hera_env_relc_road_l | 0 | km | length of roads to be relocated
hera_env_relc_rail_l | 0 | km | length of railways to be relocated
hera_env_relc_brdg_l | 0 | m | length of bridges to be relocated
hera_env_relc_tlin_l | 0 | km | length of transmission lines to be relocated
hera_env_popl_rurl_n | 0 |  | number of inhabitants affected by the reservoir in rural areas
hera_env_popl_urbn_n | 0 |  | number of inhabitants affected by the reservoir in urban areas

## io_up
Do not alter the variables names, unit or description, as well as the language label, since they are used in the HERA program
~OUT |  | Unit | en | pt | es | fr
bdg_excv_soil_up | 3.82 | $/m³ | Common excavation | Escavação comum | Excavación común | Excavation en terrain meuble
bdg_excv_rock_up | 10.57 | $/m³ | Surface rock excavation | Escavação em rocha a céu aberto | Excavación en roca superficial | Excavation em rocher
bdg_excv_ugrk_up | 70.43 | $/m³ | Underground rock excavation | Escavação em rocha subterrânea | Excavación de roca subterránea | Excavation souterraine en rocher
bdg_excv_borw_up | 7.87 | $/m³ | Borrow soil | Escavação comum em jazida | Excavación común en zona de préstamo | Excavation en zone d'emprunt
bdg_excv_qury_up | 10.77 | $/m³ | Quarry rock | Escavação em pedreira | Excavación de roca en cantera | Excavation en carrière
bdg_trtm_eart_up | 3.74 | $/m² | Foundation cleaning and treatment in dam earthworks | Limpeza e tratamento de fundações em obras de terra | Limpieza y tratamiento de fundación en obras de tierra | Préparation et traitement des fondations des travaux de terrassement
bdg_trtm_conc_up | 29.96 | $/m² | Foundation cleaning and treatment in concrete strucutures | Limpeza e tratamento de fundações em estruturas de concreto | Limpieza y tratamiento de fundación en obras de hormigón | Préparation et traitement des fondations des structures en béton
bdg_cofd_rmov_up | 3.32 | $/m³ | Cofferdam removal | A remoção de ensecadeiras | Remoción de ataguías | Enlèvement des batardeaux
bdg_cofd_01st_up | 1.91 | $/m³ | 1st phase cofferdams | Ensecadeiras da 1ª fase | Ataguías de 1a fase | Batardeaux de la 1ère phase
bdg_cofd_02nd_up | 1.66 | $/m³ | 2nd phase cofferdams | Ensecadeiras da 2ª fase | Ataguías de 2a fase | Batardeaux de la 2ème phase
bdg_eart_fill_up | 1.35 | $/m³ | Compacted earthfill | Solo compactado em barragens | Relleno de tierra compactada | Remblai compacté
bdg_rock_clay_up | 5.58 | $/m³ | Clay core | Núcleo de argila | Núcleo de arcilla | Noyau d'argile
bdg_rock_fill_up | 5.23 | $/m³ | Rockfill | Enrocamento em barragens | Relleno de enrocado | Enrochement
bdg_e0r0_fltr_up | 13.08 | $/m³ | Filters and transitions | Filtros e transições | Filtros y transiciones | Filtres et transitions
bdg_eart_ripr_up | 6.49 | $/m³ | Rip-rap or rockfill protection | Rip-rap ou enrocamento de proteção | Rip-rap o protección de enrocado | Rip-rap ou la protection du parament en enrochement
bdg_eart_prot_up | 2.97 | $/m² | Downstream face protection (grass) | Proteção da face de jusante (grama) | Protección del talud aguas abajo de la presa de tierra (pasto) | Protection du parement aval (pelouse)
bdg_conc_cemt_up | 175 | $/t | Cement | Cimento | Cemento | Ciment
bdg_conc_strc_up | 100 | $/m³ | Structural concrete | Concreto estrutural | Hormigón reforzado | Béton structural
bdg_conc_rcmc_up | 57 | $/m³ | Roller-compacted or mass concrete | Concreto compactado a rolo ou concreto massa | Hormigón compactado con rodillo o en masa | Béton compacté au rouleau ou en masse
bdg_conc_shot_up | 190 | $/m³ | Shotcrete | Concreto projetado | Concreto lanzado | Béton projeté
bdg_conc_stee_up | 2180 | $/t | Reinforcement steel | Armadura | Acero de refuerzo | Armure du béton
bdg_pstk_stee_up | 3000 | $/t | Steel lining of penstocks | Blindagem dos condutos forçados | Blindaje de la tubería forzada | Acier de la conduite forcée
bdg_accs_road_up | 217400 | $/km | Local access | Acesso local | Accesos por carretera a la central | Routes d'accès à la centrale
bdg_accs_brdg_up | 25155 | $/m | Local bridge access | Pontes de acesso local | Puentes para acceso a la central | Ponts d'accès à la centrale

## io_env
Do not alter the variables names, unit or description, as well as the language label, since they are used in the HERA program
~OUT |  | Unit | en | pt | es | fr
bdg_res0_rurl_up | 0 | $/ha | Rural properties affected by the reservoir | Propriedades rurais afetadas pelo reservatório | Propiedades rurales afectadas por el embalse | Propriétés rurales affectées par le réservoir
bdg_res0_urbn_up | 0 | $/ha | Urban properties affected by the reservoir | Propriedades urbanas afetadas pelo reservatório | Propiedades urbanas afectadas por el embalse | Propriétés urbaines affectées par le réservoir
bdg_res0_ppa0_up | 0 | $/ha | Permanent preservation areas | Áreas de preservação permanente | Área de preservación permanente | Zone de conservation permanente
bdg_relc_road_up | 150000 | $/km | Roads to be relocated | Estradas a serem relocadas | Carreteras a ser reubicadas | Routes à relocaliser
bdg_relc_rail_up | 1500000 | $/km | Railways to be relocated | Ferrovias a serem relocadas | Ferrocarriles a ser reubicados | Chemins de fer à relocaliser
bdg_relc_brdg_up | 35000 | $/m | Bridges to be relocated | Pontes a serem relocadas | Puentes a ser reubicados | Ponts à relocaliser
bdg_res0_tlin_up | 0 | $/km | Transmission lines to be relocated | Linhas de transmissão a serem relocadas | Líneas de transmisión a ser reubicadas | Lignes de transmission à relocaliser
bdg_popl_rurl_up | 20000 | $/un | Families or inhabitants affected by the reservoir in rural areas | Famílias ou habitantes atingidos pelo reservatório em zona rural | Familias o habitantes afectados por el embalse en zona rural | Familles ou les habitants touchés par le réservoir dans la zone rurale
bdg_popl_urbn_up | 25000 | $/un | Families or inhabitants affected by the reservoir in urban areas | Famílias ou habitantes atingidos pelo reservatório em zona urbana | Familias o habitantes afectados por el embalse en zona urbana | Familles ou les habitants touchés par le réservoir dans la zone urbaine
bdg_res0_clea_up | 0 | $/ha | Reservoir cleaning | Limpeza de reservatórios | La limpieza del embalse | Neettoyage du réservoir

## io_perc
Do not alter the variables names, unit or description, as well as the language label, since they are used in the HERA program
~OUT |  | Unit | en | pt | es | fr
bdg_civl_oth0_pc | 2 |  | Other costs for civil accounts | Outros custos para contas civis | Otros costos para cuentas civiles | Coûts divers pour les comptes civils
bdg_envr_oth0_pc | 30 |  | Other costs for social and environmental accounts | Outros custos para contas socioambientais | Otros costos para cuentas socioambientales | Coûts divers pour les comptes sociaux et environnementaux
bdg_civl_misc_pc | 20 |  | Miscellaneous items for civil accounts | Eventuais para contas civis | Costos eventuales para cuentas civiles | Coûts éventuels pour comptes civils
bdg_eqp0_misc_pc | 20 |  | Miscellaneous items for equipment accounts | Eventuais para contas de equipamentos | Costos eventuales para cuentas de equipos | Coûts éventuels pour les comptes d'équipement
bdg_envr_misc_pc | 20 |  | Miscellaneous items for social and environmental accounts | Eventuais para contas socioambientais | Costos eventuales para cuentas socioambientales | Coûts éventuels pour les comptes sociaux et environnementaux
bdg_indc_misc_pc | 10 |  | Miscellaneous items for indirect costs | Eventuais para indirect costs | Costos eventuales para costos indirectos | Coûts éventuels pour les coûts indirects
bdg_indc_cons_pc | 2 |  | Indirect costs for construction site and worker's camp | Custos indiretos para construção do canteiro e do acampamento | Costos indirectos para la construcción del cartel y del campamento | Coûts indirects pour le chantier de construction et le campement des travailleurs
bdg_indc_opmt_pc | 2 |  | Indirect costs for maintenance and operation of the site and the camp | Custos indiretos para manutenção e operação do canteiro e do acampamento | Costos indirectos para mantenimiento y operación del cartel y del campamento | Coûts indirects pour le fonctionnement et la maintenance du chantier et du campement
bdg_indc_engr_pc | 4 |  | Indirect costs for basic engineering | Custos indiretos para engenharia básica | Costos indirectos para la ingeniería básica | Coûts indirects pour l'ingénierie de base
bdg_indc_spec_pc | 1 |  | Indirect costs for engineering special services | Custos indiretos para serviços especiais de engenharia | Costos indirectos por servicios especiales de ingeniería | Coûts indirects pour les services spéciaux d'ingénierie
bdg_indc_envr_pc | 1.5 |  | Indirect costs for environmental projects and studies | Custos indiretos para projetos e estudos ambientais | Costos indirectos para proyectos y estudios ambientales | Coûts indirects pour les projets et les études environnementaux
bdg_indc_admn_pc | 1.5 |  | Indirect costs for owner´s administration | Custos indiretos para administração do proprietário | Costos indirectos para adminitración del propietario | Coûts indirects pour l'administration du propriétaire
bdg_intr_cons_pc | 12 |  | Interest during construction | Juros durante a construção | Interés durante la construcción | Intérêts survenus au cours de la construction

## io_conv
Do not alter the variables names, unit or description, as well as the language label, since they are used in the HERA program
~OUT |  | Unit | en | pt | es | fr
bdg_eqp0_exch_k | 0.47 |  | Exchange rate from reais to dollars for equipment costs defined by eletrobras | Taxa de câmbio (Real para Dólar) para equipamentos do manual de inventário | Tasa de cambio de reais a dólares de los costos de equipos definidos por eletrobras | Taux de change de reais en dollars des coût des équipements définis par l'eletrobras
bdg_eqp0_updt_k | 1.23 |  | Update conversion rate for equipment costs defined by eletrobras | Taxa de atualização para equipamentos do manual de inventário | Tasa de conversión de actualización de costos de equipos definidos por eletrobras | Taux d'actualization des coût des équipements définis par l'eletrobras

## unit_prices
UNIT PRICES SUMMARY
| ITEMS | UNIT | UNIT PRICE | ITEMS | UNIT | UNIT PRICE
| Common excavation | m³ | 3.82 | Rural properties | ha | 0
| Surface rock excavation | m³ | 10.57 | Urban properties | ha | 0
| Underground rock excavation | m³ | 70.43 | Permanent preservation areas | ha | 0
| Borrow soil | m³ | 7.87 | Roads | km | 150000
| Quarry rock | m³ | 10.77 | Railways | km | 1500000
| Foundation cleaning and treatment - dam earthworks | m² | 3.74 | Bridges | m | 35000
| Foundation cleaning and treatment - concrete strucutures | m² | 29.96 | Transmission lines | km | 0
| Cofferdam removal | m³ | 3.32 | Families or inhabitants in rural areas | un | 20000
| Cofferdam - 1st phase | m³ | 1.91 | Families or inhabitants in urban areas | un | 25000
| Cofferdam - 2nd phase | m³ | 1.66 | Reservoir cleaning | ha | 0
| Compacted earthfill | m³ | 1.35
| Clay core | m³ | 5.58
| Rockfill | m³ | 5.23
| Filters and transitions | m³ | 13.08
| Rip-rap or rockfill protection | m³ | 6.49
| Downstream face protection (grass) | m² | 2.97
| Cement | t | 175
| Structural concrete | m³ | 100
| Roller-compacted or mass concrete | m³ | 57
| Shotcrete | m³ | 190
| Reinforcement steel | t | 2180
| Steel lining of penstocks | t | 3000
| Local access | km | 217400
| Local bridge access | m | 25155

## summary
COSTS SUMMARY
| ITEM | UNIT | COSTS ($ x10³) | ITEM | ACCOUNT | COSTS ($ x10³)
| Common excavation | m³ | 35.526 | Lands, resettlements, relocations and other socialenvironmental costs | .10. | 0
| Surface rock excavation | m³ | 226.198 | Powerhouse civil and related land development | .11. | 5811.552
| Underground rock excavation | m³ | 746.558 | Dams and hydraulic system | .12. | 19331.0588
| Borrow soil | m³ | 0 | Diversion | .12.16 | 1293.3184
| Quarry rock | m³ | 129.24 | Dams and dikes | .12.17 | 964.1142
| Foundation cleaning and treatment - dam earthworks | m² | 45.628 | Spillway | .12.18 | 4193.5293
| Foundation cleaning and treatment - concrete strucutures | m² | 453.894 | Intakes and adduction | .12.19 | 9658.2538
| Cofferdam removal | m³ | 1.66 | Special constructions | .12.20 | 0
| Cofferdam - 1st phase | m³ | 0 | Turbines and generators | .13. | 48146.4
| Cofferdam - 2nd phase | m³ | 1.66 | Auxiliary electrical equipment | .14. | 10399.6224
| Compacted earthfill | m³ | 0 | Miscellaneous mechanical equipment | .15. | 6808.5408
| Clay core | m³ | 44.64 | Roads, railroads and bridges | .16. | 3540.36
| Rockfill | m³ | 83.68 | Direct cost |  | 94037.534
| Filters and transitions | m³ | 0 | Indirect cost | .17. | 12412.9545
| Rip-rap or rockfill protection | m³ | 0 | Total cost without interest during construction |  | 106450.4885
| Downstream face protection (grass) | m² | 0 | Interest during construction | .18. | 12774.0586
| Cement | t | 1266.65 | Total cost with interest during construction |  | 119224.5471
| Structural concrete | m³ | 2610
| Roller-compacted or mass concrete | m³ | 28.5 | Socioenvironmental cost | .10. | 0
| Shotcrete | m³ | 361 | Total civil cost | - | 17496.5708
| Reinforcement steel | t | 3283.08 | Equipment cost | - | 76540.9632
| Steel lining of penstocks | t | 1767 | Indirect cost | .17. | 12412.9545
|  |  |  | Interest during construction | .18. | 12774.0586
|  |  |  | Installed capacity | MW | 100
|  |  |  | Index cost | $/kW | 1192.2455
QUANTITIES SUMMARY
| ITEM | UNIT | QUANTITY
| Common excavation | m³ | 9300
| Surface rock excavation | m³ | 21400
| Underground rock excavation | m³ | 10600
| Borrow soil | m³ | 0
| Quarry rock | m³ | 12000
| Foundation cleaning and treatment - dam earthworks | m² | 12200
| Foundation cleaning and treatment - concrete strucutures | m² | 15150
| Cofferdam removal | m³ | 500
| Cofferdam - 1st phase | m³ | 0
| Cofferdam - 2nd phase | m³ | 1000
| Compacted earthfill | m³ | 0
| Clay core | m³ | 8000
| Rockfill | m³ | 16000
| Filters and transitions | m³ | 0
| Rip-rap or rockfill protection | m³ | 0
| Downstream face protection (grass) | m² | 0
| Cement | t | 7238
| Structural concrete | m³ | 26100
| Roller-compacted or mass concrete | m³ | 500
| Shotcrete | m³ | 1900
| Reinforcement steel | t | 1506
| Steel lining of penstocks | t | 589

## balance
CUT AND FILL VOLUMES
|  | Unit | Volume
| Rock Excavation | m³ | 32000
| Required Rockfill and Aggregates | m³ | 43112.0833
| Cofferdam - 1st phase | m³ | 0 |  | (presumed zero)
| Cofferdam - 2nd phase | m³ | 293.3333 |  | (considering 1/3 of the its volume)
| Rockfill | m³ | 14960
| Filters and transitions | m³ | 0
| Rip-rap or rockfill protection | m³ | 0
| Concrete | m³ | 27858.75
| Quarry rock | m³ | 12000 |  | (always considering 3/5 of the 1st phase cofferdam volume)
| Common Excavation | m³ | 9300
| Required Earthfill | m³ | 880
| Cofferdam - 1st phase | m³ | 0 |  | (presumed zero)
| Cofferdam - 2nd phase | m³ | 880 |  | (considering 2/3 of the its volume)
| Compacted earthfill | m³ | 0 |  | (considering 70% of its volume)
| Clay core | m³ | 0 |  | (presumed zero, already considered in its unit price)
| Borrow soil | m³ | 0 |  | (always considering 2/5 of the 1st phase cofferdam volume and 30% of the compacted earthfill volume)
Bulking Factor (BF) and Losses (L)
| Rock | Unit | BF | L
| Cofferdam - 1st phase | m³ | 0.8 | 1.1
| Cofferdam - 2nd phase | m³ | 0.8 | 1.1
| Rockfill | m³ | 0.85 | 1.1
| Filters and transitions | m³ | 0.9 | 1.15
| Rip-rap or rockfill protection | m³ | 0.85 | 1.15
| Concrete | m³ | 0.85 | 1.15
| Soil | Unit | BF | L
| Cofferdam - 1st phase | m³ | 1.2 | 1.1
| Cofferdam - 2nd phase | m³ | 1.2 | 1.1
| Compacted earthfill | m³ | 1.2 | 1.1
| Clay core | m³ | 1.2 | 1.1
Referências
|  | BQE | ELB
|  |  |  | 1,10 | rocha
|  |  | 0.83333 | 1.15 | brita
|  | 0.8 |  | 1.1
|  | 0.8 |  | 1.1
|  | 0.85 |  | 1.1
|  | 0.9 |  | 1.15
|  | 0.85 |  | 1.15
|  | 0.85 |  | 1.15
|  |  | 1.3 | 1.1
1.175
1.175
1.2
1.2

## budget
INVENTORY STUDIES
COST ESTIMATE SPREADSHEET
ACCOUNT | ITEM | UNIT | UNIT PRICE |  | COSTS | Weight in t/m3
|  |  | QUANTITY | $ | $ 10³
.10. | LANDS, RESETTLEMENTS, RELOCATIONS AND OTHER SOCIOENVIRONMENTAL ACTIONS |  |  |  | 0
.10.10 | LAND ACQUISITIONS AND LAND DEVELOPMENTS |  |  |  | 0
.10.10.10 | URBAN REAL ESTATE | gl |  |  | 0
.10.10.10.10 | Reservoir | km2 | 0 | 0 | 0
.10.10.10.11 | Construction site, workers' camp, borrow areas, etc. | ha |  |  | 0
.10.10.10.40 | Conservation Areas and Permanent Preservation Areas | ha |  |  | 0
.10.10.10.43 | Towns and villages | gl |  |  | 0
.10.10.10.44 | Isolated social and economic infrastructure | gl |  |  | 0
.10.10.10.17 | Other costs | gl |  |  | 0
.10.10.11 | RURAL REAL ESTATE | gl |  |  | 0
.10.10.11.10 | Reservoir | km2 | 0 | 0 | 0
.10.10.11.11 | Construction site, workers' camp, borrow areas, etc. | ha |  |  | 0
.10.10.11.40 | Conservation Areas and Permanent Preservation Areas | km2 | 0 | 0 | 0
.10.10.11.41 | Rural resettlement | m² |  |  | 0
.10.10.11.42 | Indigenous peoples and other ethnic groups | ha |  |  | 0
.10.10.11.43 | Towns and villages | gl |  |  | 0
.10.10.11.44 | Isolated social and economic infrastructure | gl |  |  | 0
.10.10.11.17 | Other costs | gl |  |  | 0
.10.10.12 | ACQUISITION AND LEGAL EXPENSES | % | 10 | 0 | 0
.10.10.13 | OTHER COSTS | gl |  |  | 0
.10.11 | RESETTLEMENTS AND RELOCATIONS |  |  |  | 0
.10.11.14 | ROADS | km | 0 | 150000 | 0
.10.11.15 | RAILROADS | km | 0 | 1500000 | 0
.10.11.16 | BRIDGES | m | 0 | 35000 | 0
.10.11.18 | TRANSMISSION AND DISTRIBUTION SYSTEM | km | 0 | 0 | 0
.10.11.19 | COMMUNICATIONS SYSTEM | gl |  |  | 0
.10.11.20 | POPULATION RESETTLEMENT | gl |  |  | 0
.10.11.20.41 | Rural Resettlement (families or inhabitants affected) | people | 0 | 20000 | 0
.10.11.20.42 | Indigenous peoples and other ethnic groups (families or inhabitants affected) | people |  |  | 0
.10.11.20.43 | Towns and villages (families or inhabitants affected) | people | 0 | 25000 | 0
.10.11.20.44 | Isolated social and economic infrastructure | gl |  |  | 0
.10.11.20.17 | Other costs | gl |  |  | 0
.10.11.21 | OTHER RESETTLEMENTS / RELOCATIONS | gl |  |  | 0
.10.11.13 | OTHER COSTS | gl |  |  | 0
.10.15 | OTHER SOCIOENVIRONMENTAL ACTIONS | gl |  |  | 0
.10.15.44 | SOCIOENVIRONMENTAL COMMUNICATION | gl |  |  | 0
.10.15.45 | PHYSICAL AND BIOTIC ENVIRONMENT | gl |  |  | 0
.10.15.45.18 | Reservoir Cleaning | km2 | 0 | 0 | 0
.10.15.45.40 | Conservation Areas and Permanent Preservation Areas | gl |  |  | 0
.10.15.45.45 | Conservation of flora | gl |  |  | 0
.10.15.45.46 | Conservation of fauna | gl |  |  | 0
.10.15.45.47 | Water quality | gl |  |  | 0
.10.15.45.48 | Recuperation of degraded areas | gl |  |  | 0
.10.15.45.17 | Other costs | gl |  |  | 0
.10.15.46 | SOCIOECONOMIC AND CULTURAL ENVIRONMENT | gl |  |  | 0
.10.15.46.42 | Indigenous peoples and other ethnic groups | gl |  |  | 0
.10.15.46.49 | Basic sanitation and healthcare | gl |  |  | 0
.10.15.46.50 | Housing and education infrastructure | gl |  |  | 0
.10.15.46.51 | Salvaging of cultural heritage | gl |  |  | 0
.10.15.46.52 | Support for municipalities | gl |  |  | 0
.10.15.46.17 | Other costs | gl |  |  | 0
.10.15.47 | LICENSING AND INSTITUTIONAL MANAGEMENT | gl |  |  | 0
.10.15.47.53 | Licensing | gl |  |  | 0
.10.15.47.55 | Institutional Management | gl |  |  | 0
.10.15.47.17 | Other costs | gl |  |  | 0
.10.15.48 | MULTIPLE USES | gl |  |  | 0
.10.15.13 | OTHER COSTS | % | 30 | 0 | 0 | Other socioenvironmental actions - Reservoir cleaning = 30% Environmental total costs
| Subtotal of account .10 |  |  |  | 0
.10.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .10 | % | 20 | 0 | 0
.11. | POWERHOUSE (CIVIL CONSTRUCTION) AND RELATED LAND DEVELOPMENTS |  |  |  | 5811.552
.11.12 | LAND DEVELOPMENTS IN THE PLANT AREA | gl | 1 | 929000 | 929
.11.13 | POWERHOUSE | gl |  |  | 3913.96
.11.13.00.12 | Excavation | gl |  |  | 120.98
.11.13.00.12.10 | Common | m³ | 4000 | 3.82 | 15.28
.11.13.00.12.11 | Surface rock | m³ | 10000 | 10.57 | 105.7
.11.13.00.12.12 | Underground rock | m³ | 0 | 70.43 | 0
.11.13.00.13 | Foundation cleaning and treatment | m² | 500 | 29.96 | 14.98
.11.13.00.14 | Concrete | gl |  |  | 2528
.11.13.00.14.13 | Cement | t | 2400 | 175 | 420 | 0.3
.11.13.00.14.14 | Concrete without cement | m³ | 8000 | 100 | 800
.11.13.00.14.15 | Reinforcement steel | t | 600 | 2180 | 1308 | 0.075
.11.13.00.15 | Installations and final works | gl | 1 | 1250000 | 1250
| Subtotal of Account .11 |  |  |  | 4842.96
.11.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .11 | % | 20 | 4842960 | 968.592
.12. | DAMS AND INTAKES |  |  |  | 19331.0588
.12.16 | RIVER DIVERSION |  |  |  | 1293.3184
.12.16.22 | COFFERDAMS | gl |  |  | 3.569
.12.16.22.12 | Concrete for deflector baffle | gl |  |  | 0
.12.16.22.19 | Earth-rock cofferdam 1st Phase | m³ | 0 | 1.91 | 0
.12.16.22.19 | Earth-rock cofferdam 2nd Phase | m³ | 1000 | 1.66 | 1.66
.12.16.22.20 | Special cofferdams | gl |  |  | 0
.12.16.22.21 | Removal of cofferdams | m³ | 500 | 3.32 | 1.66
.12.16.22.22 | Dewatering and other costs | % | 15 | 1660 | 0.249
.12.16.22.56 | Service bridge | gl |  |  | 0
.12.16.23 | DIVERSION TUNNEL | gl |  |  | 1289.7494
.12.16.23.12 | Excavation | gl |  |  | 221.63
.12.16.23.12.10 | Common | m³ | 1600 | 3.82 | 6.112
.12.16.23.12.11 | Surface rock | m³ | 400 | 10.57 | 4.228
.12.16.23.12.12 | Underground rock | m³ | 3000 | 70.43 | 211.29
.12.16.23.13 | Foundation cleaning and treatment | m² | 100 | 3.74 | 0.374
.12.16.23.14 | Concrete | gl |  |  | 129.36
.12.16.23.14.13 | Cement | t | 112 | 175 | 19.6 | 0.28
.12.16.23.14.14 | Concrete without cement | m³ | 400 | 100 | 40
.12.16.23.14.15 | Reinforcement steel | t | 32 | 2180 | 69.76 | 0.08
.12.16.23.14 | Shotcrete | gl |  |  | 118.53
.12.16.23.14.13 | Cement | t | 90 | 175 | 15.75 | 0.3
.12.16.23.14.14 | Concrete without cement | m³ | 300 | 190 | 57
.12.16.23.14.15 | Reinforcement steel | t | 21 | 2180 | 45.78 | 0.07
.12.16.23.14 | Dental Concrete | gl |  |  | 41.625
.12.16.23.14.13 | Cement | t | 75 | 175 | 13.125 | 0.15
.12.16.23.14.14 | Concrete without cement | m³ | 500 | 57 | 28.5
.12.16.23.23 | Gates and related closing equipment | gl |  |  | 768
.12.16.23.23.16 | Fixed wheel gates | un | 1 | 358000 | 358
.12.16.23.23.17 | Stoplogs | un | 1 | 258000 | 258
.12.16.23.23.56 | Other embedded parts | un | 1 | 152000 | 152
.12.16.23.17 | Other costs | % | 2 | 511519 | 10.2304
.12.16.24 | DIVERSION CHANNEL OR GALLERY / SLUICEWAY | gl |  |  | 0
.12.16.24.12 | Excavation | gl |  |  | 0
.12.16.24.12.10 | Common | m³ | 0 | 3.82 | 0
.12.16.24.12.11 | Surface rock | m³ | 0 | 10.57 | 0
.12.16.24.13 | Foundation cleaning and treatment | m² | 0 | 29.96 | 0
.12.16.24.14 | Concrete | gl |  |  | 0
.12.16.24.14.13 | Cement | t | 0 | 175 | 0 | 0.28
.12.16.24.14.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.16.24.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.08
.12.16.24.14 | Dental Concrete | gl |  |  | 0
.12.16.24.14.13 | Cement | t | 0 | 175 | 0 | 0.15
.12.16.24.14.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.16.24.23 | Gates and related closing equipment | gl |  |  | 0
.12.16.24.23.16 | Fixed wheel gates | un | 0 | 0 | 0
.12.16.24.23.17 | Stoplogs | un | 0 | 0 | 0
.12.16.24.23.17 | Downstream stoplogs | un | 0 | 0 | 0
.12.16.24.23.56 | Other embedded parts | un | 1 | 0 | 0
.12.16.24.17 | Other costs | % | 2 | 0 | 0
.12.17 | DAMS AND DIKES |  |  |  | 964.1142
.12.17.25 | EARTHFILL AND ROCKFILL DAMS AND DIKES | gl |  |  | 262.7112
.12.17.25.12 | Excavation | gl |  |  | 129.24
.12.17.25.12.10 | Common | m³ | 0 | 3.82 | 0
.12.17.25.12.10 | Borrow soil | m³ | 0 | 7.87 | 0
.12.17.25.12.11 | Surface Rock | m³ | 0 | 10.57 | 0
.12.17.25.12.11 | Quarry Rock | m³ | 12000 | 10.77 | 129.24
.12.17.25.13 | Foundation cleaning and treatment | m² | 0 | 3.74 | 0
.12.17.25.24 | Compacted Earthfill | m³ | 0 | 1.35 | 0
.12.17.25.25 | Rockfill | m³ | 16000 | 5.23 | 83.68
.12.17.25.26 | Clay Core | m³ | 8000 | 5.58 | 44.64
.12.17.25.29 | Filters / Transitions | m³ | 0 | 13.08 | 0
.12.17.25.27 | Concrete face | gl |  |  | 0
.12.17.25.27.13 | Cement | t | 0 | 175 | 0 | 0.25
.12.17.25.27.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.17.25.27.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.08
.12.17.25.32 | Proteccion of dam faces | gl |  |  | 0
.12.17.25.32.18 | Upstream Face | m3 | 0 | 6.49 | 0
.12.17.25.32.19 | Downstream Face | m2 | 0 | 2.97 | 0
.12.17.25.17 | Other costs | % | 2 | 257560 | 5.1512
.12.17.26 | CONCRETE DAMS | gl |  |  | 0
.12.17.26.12 | Excavation | gl |  |  | 0
.12.17.26.12.10 | Common | m³ | 0 | 3.82 | 0
.12.17.26.12.11 | Surface Rock | m³ | 0 | 10.57 | 0
.12.17.26.13 | Foundation cleaning and treatment | m² | 0 | 29.96 | 0
.12.17.26.14 | Concrete | gl |  |  | 0
.12.17.26.14.13 | Cement | t | 0 | 175 | 0 | 0.25
.12.17.26.14.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.17.26.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.01
.12.17.26.15 | Roller Compacted Concrete | gl |  |  | 0
.12.17.26.15.13 | Cement | t | 0 | 175 | 0 | 0.1
.12.17.26.15.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.17.26.17 | Other costs | % | 2 | 0 | 0
.12.17.27 | CONCRETE TRANSITIONS AND RETAINING WALLS | gl |  |  | 701.403
.12.17.27.12 | Excavation | gl |  |  | 35.53
.12.17.27.12.10 | Common | m³ | 1000 | 3.82 | 3.82
.12.17.27.12.11 | Surface Rock | m³ | 3000 | 10.57 | 31.71
.12.17.27.13 | Foundation cleaning and treatment | m² | 2000 | 29.96 | 59.92
.12.17.27.14 | Concrete | gl |  |  | 592.2
.12.17.27.14.13 | Cement | t | 600 | 175 | 105 | 0.15
.12.17.27.14.14 | Concrete without cement | m³ | 4000 | 100 | 400
.12.17.27.14.15 | Reinforcement steel | t | 40 | 2180 | 87.2 | 0.01
.12.17.27.17 | Other costs | % | 2 | 687650 | 13.753
.12.18 | SPILLWAYS |  |  |  | 4193.5293
.12.18.28 | SURFACE SPILLWAYS | gl |  |  | 4193.5293
.12.18.28.12 | Excavation | gl |  |  | 53.295
.12.18.28.12.10 | Common | m³ | 1500 | 3.82 | 5.73
.12.18.28.12.11 | Surface Rock | m³ | 4500 | 10.57 | 47.565
.12.18.28.13 | Foundation cleaning and treatment | m² | 2000 | 29.96 | 59.92
.12.18.28.14 | Concrete | gl |  |  | 2527.5
.12.18.28.14.13 | Cement | t | 2500 | 175 | 437.5 | 0.25
.12.18.28.14.14 | Concrete without cement | m³ | 10000 | 100 | 1000
.12.18.28.14.15 | Reinforcement steel | t | 500 | 2180 | 1090 | 0.05
.12.16.28.14 | Dental Concrete | gl |  |  | 0
.12.16.28.14.13 | Cement | t | 0 | 175 | 0 | 0.15
.12.16.28.14.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.18.28.23 | Gates and related closing equipment | gl |  |  | 1500
.12.18.28.23.16 | Segment gate | un | 2 | 429000 | 858
.12.18.28.23.17 | Stoplog | un | 1 | 186000 | 186
.12.18.28.23.20 | Crane | un | 1 | 268000 | 268
.12.18.28.23.56 | Other embedded parts | un | 1 | 188000 | 188
.12.18.28.17 | Other costs | % | 2 | 2640715 | 52.8143
.12.18.29 | OTHER SPILLWAYS | gl |  |  | 0
.12.18.29.12 | Excavation | gl |  |  | 0
.12.18.29.12.10 | Common | m³ | 0 | 3.82 | 0
.12.18.29.12.11 | Surface Rock | m³ | 0 | 10.57 | 0
.12.18.29.13 | Foundation cleaning and treatment | m² | 0 | 29.96 | 0
.12.18.29.14 | Concrete | gl |  |  | 0
.12.18.29.14.13 | Cement | t | 0 | 175 | 0 | 0.25
.12.18.29.14.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.18.29.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.05
.12.18.29.23 | Gates and related closing equipment | gl |  |  | 0
.12.18.29.23.16 | Fixed wheel gates | un |  |  | 0
.12.18.29.23.17 | Stoplog | un |  |  | 0
.12.18.29.23.20 | Crane | un | 1 |  | 0
.12.18.29.23.56 | Other embedded parts | un | 1 |  | 0
.12.18.29.17 | Other costs | % | 2 | 0 | 0
.12.19 | INTAKE AND HYDRAULIC SYSTEM |  |  |  | 9658.2538
.12.19.30 | INTAKE | gl |  |  | 1333.1275
.12.19.30.12 | Excavation | gl |  |  | 8.927
.12.19.30.12.10 | Common | m³ | 400 | 3.82 | 1.528
.12.19.30.12.11 | Surface Rock | m³ | 700 | 10.57 | 7.399
.12.19.30.13 | Foundation cleaning and treatment | m² | 100 | 29.96 | 2.996
.12.19.30.14 | Concrete | gl |  |  | 283.3
.12.19.30.14.13 | Cement | t | 300 | 175 | 52.5 | 0.3
.12.19.30.14.14 | Concrete without cement | m³ | 1000 | 100 | 100
.12.19.30.14.15 | Reinforcement steel | t | 60 | 2180 | 130.8 | 0.06
.12.16.30.14 | Dental Concrete | gl |  |  | 0
.12.16.30.14.13 | Cement | t | 0 | 175 | 0 | 0.15
.12.16.30.14.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.19.30.23 | Gates and related closing equipment | gl |  |  | 1032
.12.19.30.23.16 | Fixed wheel gates | un | 2 | 173000 | 346
.12.19.30.23.17 | Stoplogs | un | 1 | 20000 | 20
.12.19.30.23.56 | Other embedded parts | un | 1 | 170000 | 170
.12.19.30.23.20 | Crane | un | 1 | 95000 | 95
.12.19.30.23.21 | Trash racks and trash racks cleaner | un | 1 | 401000 | 401
.12.19.30.17 | Other costs | % | 2 | 295223 | 5.9045
.12.19.31 | HEADRACE CHANNEL AND FOREBAY | gl |  |  | 909.9556
.12.19.31.12 | Excavation | gl |  |  | 0
.12.19.31.12.10 | Common | m³ | 0 | 3.82 | 0
.12.19.31.12.11 | Surface Rock | m³ | 0 | 10.57 | 0
.12.19.31.13 | Foundation cleaning and treatment | m² | 10550 | 5.1069 | 53.878
.12.19.31.14 | Concrete | gl |  |  | 0
.12.19.31.14.13 | Cement | t | 0 | 175 | 0 | 0.25
.12.19.31.14.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.19.31.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.05
.12.19.31.14 | Shotcrete | gl |  |  | 0
.12.19.31.14.13 | Cement | t | 0 | 175 | 0 | 0.3
.12.19.31.14.14 | Concrete without cement | m³ | 0 | 190 | 0
.12.19.31.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.07
.12.19.31.14 | Dental Concrete | gl |  |  | 0
.12.19.31.14.13 | Cement | t | 0 | 175 | 0 | 0.15
.12.19.31.14.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.19.31.23 | Gates and related closing equipment | gl |  |  | 855
.12.19.31.23.16 | Fixed wheel gates | un | 2 | 150000 | 300
.12.19.31.23.17 | Stoplogs | un | 1 | 15000 | 15
.12.19.31.23.56 | Other embedded parts | un | 1 | 120000 | 120
.12.19.31.23.20 | Crane | un | 1 | 70000 | 70
.12.19.31.23.21 | Trash racks and trash racks cleaner | un | 1 | 350000 | 350
.12.19.31.17 | Other costs | % | 2 | 53878 | 1.0776
.12.19.32 | LOW PRESSURE TUNNEL OR PENSTOCK | gl |  |  | 1090.6554
.12.19.31.12 | Excavation | gl |  |  | 281.72
.12.19.31.12.10 | Common | m³ | 0 | 3.82 | 0
.12.19.31.12.11 | Surface Rock | m³ | 0 | 10.57 | 0
.12.19.31.12.12 | Underground rock | m³ | 4000 | 70.43 | 281.72
.12.19.31.13 | Foundation cleaning and treatment | m² | 1000 | 3.74 | 3.74
.12.19.31.14 | Concrete | gl |  |  | 151.65
.12.19.31.14.13 | Cement | t | 150 | 175 | 26.25 | 0.25
.12.19.31.14.14 | Concrete without cement | m³ | 600 | 100 | 60
.12.19.31.14.15 | Reinforcement steel | t | 30 | 2180 | 65.4 | 0.05
.12.19.31.14 | Shotcrete | gl |  |  | 632.16
.12.19.31.14.13 | Cement | t | 480 | 175 | 84 | 0.3
.12.19.31.14.14 | Concrete without cement | m³ | 1600 | 190 | 304
.12.19.31.14.15 | Reinforcement steel | t | 112 | 2180 | 244.16 | 0.07
.12.19.31.17 | Other costs | % | 2 | 1069270 | 21.3854
.12.19.33 | SURGE TANK | gl |  |  | 460.683
.12.19.31.12 | Excavation | gl |  |  | 47.25
.12.19.31.12.10 | Common | m³ | 200 | 3.82 | 0.764
.12.19.31.12.11 | Surface Rock | m³ | 400 | 10.57 | 4.228
.12.19.31.12.12 | Underground rock | m³ | 600 | 70.43 | 42.258
.12.19.31.13 | Foundation cleaning and treatment | m² | 0 | 29.96 | 0
.12.19.31.14 | Concrete | gl |  |  | 404.4
.12.19.31.14.13 | Cement | t | 400 | 175 | 70 | 0.25
.12.19.31.14.14 | Concrete without cement | m³ | 1600 | 100 | 160
.12.19.31.14.15 | Reinforcement steel | t | 80 | 2180 | 174.4 | 0.05
.12.19.30.23 | Gates and related closing equipment | gl |  |  | 0
.12.19.30.23.23 | Steel Lining | t | 0 | 3000 | 0
.12.19.31.17 | Other costs | % | 2 | 451650 | 9.033
.12.19.34 | HIGH PRESSURE TUNNEL AND PENSTOCK | gl |  |  | 5858.3591
.12.19.31.12 | Excavation | gl |  |  | 233.958
.12.19.31.12.10 | Common | m³ | 400 | 3.82 | 1.528
.12.19.31.12.11 | Surface Rock | m³ | 2000 | 10.57 | 21.14
.12.19.31.12.12 | Underground rock | m³ | 3000 | 70.43 | 211.29
.12.19.31.13 | Foundation cleaning and treatment | m² | 11000 | 27.5764 | 303.34
.12.19.31.14 | Concrete | gl |  |  | 140.505
.12.19.31.14.13 | Cement | t | 131 | 175 | 22.925 | 0.262
.12.19.31.14.14 | Concrete without cement | m³ | 500 | 100 | 50
.12.19.31.14.15 | Reinforcement steel | t | 31 | 2180 | 67.58 | 0.062
.12.19.30.23 | Gates and related closing equipment | gl |  |  | 5167
.12.19.30.23.23 | Steel Lining | t | 589 | 3000 | 1767
.12.19.30.23.24 | Butterfly valve | un | 2 | 1700000 | 3400
.12.19.30.23.24 | Spherical valve | un | 0 | 0 | 0
.12.19.31.17 | Other costs | % | 2 | 677803 | 13.5561
.12.19.35 | TAILRACE CHANNEL OR TUNNEL | gl |  |  | 5.4733
.12.19.35.12 | Excavation | gl |  |  | 4.992
.12.19.35.12.10 | Common | m³ | 200 | 3.82 | 0.764
.12.19.35.12.11 | Surface Rock | m³ | 400 | 10.57 | 4.228
.12.19.35.12.12 | Underground rock | m³ | 0 | 70.43 | 0
.12.19.35.13 | Foundation cleaning and treatment | m² | 100 | 3.74 | 0.374
.12.19.35.14 | Concrete | gl |  |  | 0
.12.19.35.14.13 | Cement | t | 0 | 175 | 0 | 0.25
.12.19.35.14.14 | Concrete without cement | m³ | 0 | 100 | 0
.12.19.35.14.15 | Reinforcement steel | t | 0 | 2180 | 0 | 0.05
.12.16.35.14 | Dental Concrete | gl |  |  | 0
.12.16.35.14.13 | Cement | t | 0 | 175 | 0 | 0.15
.12.16.35.14.14 | Concrete without cement | m³ | 0 | 57 | 0
.12.19.35.17 | Other costs | % | 2 | 5366 | 0.10732
.12.20 | SPECIAL CONSTRUCTIONS |  |  |  | 0
.12.20.36 | LOCK AND / OR PORT | gl | 1 | 0 | 0
.12.20.37 | OTHER SPECIAL CONSTRUCTIONS | gl | 1 | 0 | 0
| Subtotal for civil construction works |  |  |  | 6787.2157
| Subtotal for equipment |  |  |  | 9322
.12.27.98 | MISCELLANEOUS ITEMS FROM ACCOUNT .12 civil construction works | % | 20 | 6787215.68 | 1357.4431
.12.27.99 | MISCELLANEOUS ITEMS FROM ACCOUNT .12 equipment | % | 20 | 9322000 | 1864.4
.13. | TURBINES E GENERATORS |  |  |  | 48146.4
.13.13.00.23.17 | Fixed wheel gates | un | 2 | 84000 | 168
.13.13.00.23.20 | Crane | un |  |  | 0
.13.13.00.23.28 | Turbines | un | 2 | 7180000 | 14360
.13.13.00.23.29 | Generators | un | 2 | 12580000 | 25160
.13.13.00.23.56 | Other embedded parts | gl | 1 | 434000 | 434
| Subtotal of Account .13 |  |  |  | 40122
.13.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .13 | % | 20 | 40122000 | 8024.4
.14. | AUXILIARY ELETRICAL EQUIPMENT |  |  |  | 10399.6224
.14.00.00.23.30 | Auxiliary eletric equipment | % | 18 | 48146400 | 8666.352
| Subtotal of Account .14 |  |  |  | 8666.352
.14.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .14 | % | 20 | 8666352 | 1733.2704
.15. | MISCELLANEOUS MECHANICAL EQUIPMENT |  |  |  | 6808.5408
.15.13.00.23.20 | Bridge crane | un | 1 | 922000 | 922
.15.13.00.23.20 | Gantry crane | un | 1 | 1863000 | 1863
.15.00.00.23.31 | Miscellaneous equipment | % | 6 | 48146400 | 2888.784
| Subtotal of Account .15 |  |  |  | 5673.784
.15.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .15 | % | 20 | 5673784 | 1134.7568
.16. | ROADS, RAILROADS AND BRIDGES |  |  |  | 3540.36
.16.00.14 | ROADS | km | 2 | 217400 | 434.8
.16.00.15 | RAILROADS | km |  |  | 0
.16.00.16 | BRIDGES | m | 100 | 25155 | 2515.5
.16.00.17 | AIRPORT | km |  |  | 0
| Subtotal of Account .16 |  |  |  | 2950.3
.16.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .16 | % | 20 | 2950300 | 590.06
| TOTAL DIRECT COSTS |  |  |  | 94037.534
.17. | INDIRECT COSTS |  |  |  | 12412.9545
.17.21 | CONSTRUCTION SITE AND WORKERS' CAMP |  |  |  | 3761.5014
.17.21.38 | CONSTRUCTION | % | 2 | 94037534.016 | 1880.7507
.17.21.39 | MAINTENANCE AND OPERATION | % | 2 | 94037534.016 | 1880.7507
.17.22 | OWNER'S ENGINEERING AND ADMINISTRATION |  |  |  | 7523.0027
.17.22.40 | ENGINEERING | gl |  |  | 6112.4397
.17.22.40.36 | Basic engineering project | % | 4 | 94037534.016 | 3761.5014
.17.22.40.37 | Special engineering services | % | 1 | 94037534.016 | 940.3753
.17.22.40.54 | Environmental studies and projects | % | 1.5 | 94037534.016 | 1410.563
.17.22.41 | OWNER'S ADMINISTRATON | % | 1.5 | 94037534.016 | 1410.563
| Subtotal of Account .17 |  |  |  | 11284.5041
.17.27 | MISCELLANEOUS ITEMS FROM ACCOUNT .17 | % | 10 | 11284504.0819 | 1128.4504
| DIRECT AND INDIRECT COSTS |  |  |  | 106450.4885
.18. | INTEREST DURING CONSTRUCTION | % | 12 | 106450488.5061 | 12774.0586
| TOTAL COST INCLUDING INTEREST |  |  |  | 119224.5471
| Installed Capacity | kW | 100000
| Index cost ($/kW) |  |  |  | 1192.2455